# ANNEX IV: Budget breakdown (Model financial offer)

In compliance with the technical offer [c4f_annexiitechspeciiitechoffer_en_1]

Page No 1 [of 12]

PUBLICATION REFERENCE: VIS/004/MAE/2018/1PAL449 (1-2 Lot)	NAME OF TENDERER: <name>

LOT 1. Delivery to 3 Industrial Schools

|  | Main Equipment | Nablus Qty | Jenin Qty | DDSIS Qty | Total Qty | Unit Price (UNIT COSTS WITH DELIVERY DDP VAT UNPAID) EUR | Total Price (TOTAL COST WITH DELIVERY DDP VAT UNPAID) EUR |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Solar panels |  |  |  |  |  |  |
|  | 72 cell Solar Panels, Efficiency not less than 325Wp.Tier One, Top Ten enlisted Solar panels, PID Certification according to IE62804, 12 years workmanship warranty, 25 years production warranty. | 36 | 36 | 6 | 78 |  |  |
| 2 | Structure |  |  |  |  |  |  |
| A | Galvanized steel not less than 2mm thickness, as per attached drawings, (alternatives to withstand 120km/h wind speed are accepted after test report), prefabricated concrete blocks 4 units per triangle. Structure includes all accessories and screws and bolts and nuts and washers, Supply without Installation. suitable structure for 18 Solar Panels Inclination 20 degrees. | 1 | 1 | 0 | 2 |  |  |
| B | As Above, for 18 Solar Panels Inclination 40 degrees. | 1 | 1 | 0 | 2 |  |  |
| 3 | Off-Grid Inverter/Charger |  |  |  |  |  |  |
|  | Combi Inverter/Charger, 5kVA AC output Power, MPPT Charger suitable for not less than 3000Wp PV power, 92% Efficiency, Capacity to Charge Batteries from the Grid, 48VDC Nominal Voltage, 2 years warranty. | 3 | 3 | 0 | 6 |  |  |
| 4 | Synchronization Kit |  |  |  |  |  |  |
|  | Synchronization equipment suitable to connect the three Inverter/Chargers, into a 3 phase system, compatible with supplied inverter/Chargers, 2 years warranty | 1 | 1 | 1 | 3 |  |  |
| 5 | Off-Grid Inverter |  |  |  |  |  |  |
|  | 24VDC Nominal inverter, efficiency not less than 92%, output AC Not less than 1500W, NO Charger capability should be present. 2 years warranty. | 3 | 3 | 3 | 9 |  |  |
| 6 | Solar Charger MPPT |  |  |  |  |  |  |
|  | 45A Solar Battery Charger, MPPT Charging capability, adjustable Battery Nominal Voltage System 12/24/48VDC, configurable Charger Mode, 5years warranty, | 3 | 3 | 3 | 9 |  |  |
| 7 | Solar Charger PWM |  |  |  |  |  |  |
|  | 45A Solar Battery Charger, PWM Charging capability, adjustable Battery Nominal Voltage System 12/24/48VDC, configurable Charger Mode, 5years warranty, | 3 | 3 | 3 | 9 |  |  |
| 8 | Solar Batteries |  |  |  |  |  |  |
|  | Deep Cycle Battery, 100Ah@C20, 12VDC, 1000Cycle @50%DoD, 2 years warranty. | 12 | 12 | 0 | 24 |  |  |
| 9 | on-grid inverter |  |  |  |  |  |  |
|  | 2-3 kWn Grid tied string Inverter, start up and operating Voltage suitable to operate with only 6 solar panels in series, compatible with offered solar panels, 5 years warranty, Inverter with existing technical service in The country since more than 8 years. | 3 | 3 | 0 | 6 |  |  |
| 10 | Monitoring Datalogger |  |  |  |  |  |  |
|  | Capable of monitoring On-Grid Inverters, Capable of Monitoring Weather stations, 2 years warranty, Ethernet adapted, Web based monitoring. | 1 | 1 | 0 | 2 |  |  |
| 11 | weather station |  |  |  |  |  |  |
|  | Compatible with data logger, capable of monitoring Solar irradiance Tilted, and capable of monitoring horizontal Irradiance (two irradiance sensors in total), capable of monitoring wind speed, capable of monitoring ambient and panel temperature, Including all of the sensors and accessories, 5 years warranty |  |  |  |  |  |  |
| A | Irradiance sensor | 2 | 2 | 0 | 4 |  |  |
| B | panel temp sensor | 2 | 2 | 0 | 4 |  |  |
| C | Wind speed sensor | 1 | 1 | 0 | 2 |  |  |
| D | ambient temperature sensor | 1 | 1 | 0 | 2 |  |  |
|  | Protections |  |  |  |  |  |  |
| 12 | Energy Meter Direct single |  |  |  |  |  |  |
|  | single phase AC, Direct, 40A or more, unidirectional. | 4 | 4 | 0 | 8 |  |  |
| 13 | Energy Meter Direct 3 phase |  |  |  |  |  |  |
|  | three phase AC, Direct, 40A or more, unidirectional. | 4 | 4 | 0 | 8 |  |  |
| 14 | Energy Meter Indirect 3 phase analyzer |  |  |  |  |  |  |
|  | Three Phase AC, Indirect, bidirectional, analyzer, power factor, active and reactive power, clear Import and export Energy, power, current, Voltage analyze per phase. | 4 | 4 | 1 | 9 |  |  |
| 15 | Current Transformer |  |  |  |  |  |  |
|  | 5 to 60 current transformers. | 12 | 12 | 3 | 27 |  |  |
| 16 | DC Breakers |  |  |  |  |  |  |
|  | 800VDC Operating Voltage, 2 pole breakers, amp capacities |  |  |  |  |  |  |
| A | 13A | 6 | 6 | 3 | 15 |  |  |
| B | 40A | 3 | 3 | 3 | 9 |  |  |
| C | 63A | 6 | 6 | 3 | 15 |  |  |
| D | 100A | 3 | 3 | 3 | 9 |  |  |
| 17 | DC Surge Arrester |  |  |  |  |  |  |
|  | Type II Surge arrester, DC Compatible, Special for PV systems, 600VDC at least, 40kA. | 6 | 6 | 3 | 15 |  |  |
| 18 | DC Fuse Holder |  |  |  |  |  |  |
|  | DC Fuse Holder, up to 63A, 1000VDC, 2 Pole | 20 | 20 | 15 | 52 |  |  |
| 19 | DC Fuse |  |  |  |  |  |  |
|  | DC Fuse, 1000VDC, 16A, Cylindrical | 50 | 50 | 50 | 150 |  |  |
| 20 | AC Breaker single phase |  |  |  |  |  |  |
|  | 2 pole breaker, AC, 250VAC, curve C, amp capacities |  |  |  |  |  |  |
| A | 16A | 9 | 9 | 0 | 18 |  |  |
| B | 32A | 18 | 18 | 0 | 36 |  |  |
| 21 | AC Breaker single phase Transfer switch |  |  |  |  |  |  |
|  | 3 stage, 2 Pole Breaker, AC, Single Phase, 32A | 0 | 0 | 18 | 18 |  |  |
| 22 | AC Surge Arrester single phase, |  |  |  |  |  |  |
|  | 2 Pole, 40kA, Type II, single phase, | 6 | 6 | 2 | 14 |  |  |
| 23 | AC Breaker 3 phase |  |  |  |  |  |  |
|  | 4 Pole, 3 phase, AC Breaker, Curve C, Amp capacities |  |  |  |  |  |  |
| A | 16A | 9 | 9 | 0 | 18 |  |  |
| B | 32A | 3 | 3 | 0 | 6 |  |  |
| C | 50A | 3 | 3 | 0 | 6 |  |  |
| 24 | AC Surge Arrester 3 phase |  |  |  |  |  |  |
|  | 4Pole, 40kA, AC, 3 phase, Type II | 4 | 4 | 2 | 10 |  |  |
|  | Boxes |  |  |  |  |  |  |
| 25 | IP 65 Water proof box, with DIN Rails included, with buss bars included, With access to breakers without the need to un-install the cover, (breaker windows), 12 Slots | 18 | 18 | 9 | 45 |  |  |
| 26 | IP 65 Water proof box, with DIN Rails included, with buss bars included, With access to breakers without the need to un-install the cover, (breaker windows), 24 Slots | 12 | 12 | 9 | 33 |  |  |
| 27 | IP65 Water proof Box, empty, CI4, transparent cover | 6 | 6 | 3 | 15 |  |  |
| 28 | IP55 Earth Box, D2. | 6 | 6 | 3 | 15 |  |  |
| 29 | Main Panel Box, Plastic, 60 Slots, with DIN Rails, with Buss bars, with panel, IP65 | 4 | 4 | 0 | 8 |  |  |
| 30 | Cable Glands, sizes |  |  |  |  |  |  |
| A | 1/2" | 50 | 50 | 20 | 120 |  |  |
| B | 3/4" | 50 | 50 | 20 | 120 |  |  |
| C | 1" | 50 | 50 | 20 | 120 |  |  |
| D | 1.25" | 12 | 12 | 6 | 30 |  |  |
| 31 | PVC Trunk 12*6 | 30 | 30 | 0 | 60 |  |  |
| 32 | PVC Trunk 6*4 | 30 | 30 | 0 | 60 |  |  |
| 33 | Earth Buss bar, 4cm wide, with screws. | 6 | 6 | 3 | 15 |  |  |
| 34 | DIN Buss Bar, 2P, 11 screws | 3 | 3 | 2 | 8 |  |  |
| 35 | DIN Buss Bar, 5P, 11 screws | 3 | 3 | 2 | 8 |  |  |
|  | Cables |  |  |  |  |  |  |
| 36 | Solar Cable, PV1-F, (meters) |  |  |  |  |  |  |
| A | 6mm Black | 1000 | 1000 | 500 | 2500 |  |  |
| B | 6mm Red | 1000 | 1000 | 500 | 2500 |  |  |
| C | 25mm Black | 50 | 50 | 20 | 120 |  |  |
| D | 25mm Red | 50 | 50 | 20 | 120 |  |  |
| 37 | XLP Cables, double Insulation, Copper, (meters) |  |  |  |  |  |  |
| A | 3x6 | 100 | 100 | 0 | 200 |  |  |
| B | 5x6 | 60 | 60 | 0 | 120 |  |  |
| 38 | Earth Cables, single, multicore, Yellow/Green, copper,(meters) |  |  |  |  |  |  |
| A | 10mm | 100 | 100 | 100 | 300 |  |  |
| B | 16mm | 100 | 100 | 0 | 200 |  |  |
| 39 | Flexible Cables, single insulation Copper, (meters) |  |  |  |  |  |  |
| A | 6mm brown | 100 | 100 | 50 | 250 |  |  |
| B | 6mm Blue | 100 | 100 | 50 | 250 |  |  |
| C | 6mm Green/Yellow | 100 | 100 | 100 | 300 |  |  |
| D | 10mm Green/Yellow | 100 | 100 | 100 | 300 |  |  |
| E | Ethernet cable Cat6, double jacket outdoor | 300 | 300 | 300 | 900 |  |  |
|  | Tools |  |  |  |  |  |  |
|  | PC Computer |  |  |  |  |  |  |
| 40 | i7, 8th Generation, desktop, HD, 512Gb SSD. 21" Screen, Ram 16GB, GTX1070 Graphic card, Intel motherboard, All equipment from the same Band. Wireless mouse and keyboard. | 3 | 3 | 1 | 7 |  |  |
| 41 | Bosh/Makitta; Kit (angle grinder cut/rotary Hammer /hammer drill driver kit) with two 6Ah/18V Batteries | 2 | 2 | 0 | 4 |  |  |
| 42 | MC4 Crimping Tool, to crimp 4 & 6 mm cables | 1 | 1 | 1 | 3 |  |  |
| 43 | Clamp meter, 1000VDC, 600A(DC/AC) | 3 | 3 | 0 | 6 |  |  |
| 44 | Earth Loop tester | 1 | 1 | 1 | 3 |  |  |
| 45 | crimping pliers for Insulated terminals (1.5-6mm) | 3 | 3 | 3 | 9 |  |  |
| 46 | crimping tool for cable lugs (6-50mm) | 1 | 1 | 1 | 3 |  |  |
| 47 | Metallic Box or specialized Bag, for tools accessories, to contain | 1 | 1 | 0 | 2 |  |  |
| 48 | Deep socket 1/2" DR sizes (set) (8/9/10/11/12/13/14/15/16/17/18/19/20) | 1 | 1 | 0 | 2 |  |  |
| 49 | star key wrench folding set (TH9-10-15-20-25-27-30-40) | 1 | 1 | 0 | 2 |  |  |
| 50 | Hex key wrench folding set 7pc (2.5/3/4/5/6/8/10mm) | 1 | 1 | 1 | 3 |  |  |
| 51 | Holley star key wrench folding set | 1 | 1 | 0 | 2 |  |  |
| 52 | Gear Ring-Open end wrench sizes (9/10/11/12/13/14/15) (Set) | 1 | 1 | 0 | 2 |  |  |
| 53 | Set of CRV adapters 1/2" / 1/4 " / 3/8" | 1 | 1 | 1 | 3 |  |  |
| 54 | Step drill 4mm-32mm with impact ready | 1 | 1 | 1 | 3 |  |  |
| 55 | step drill 4mm-32mm with drill ready | 1 | 1 | 1 | 3 |  |  |
| 56 | Adapter for Rotary hammer to hold Masonry Bits | 2 | 2 | 1 | 5 |  |  |
| 57 | sockets ready to be installed on hammer drill driver kit, with magnet sizes (3/8" / 13mm / 15mm) (3 units total) | 2 | 2 | 1 | 5 |  |  |
| 58 | Magnetic power screw driving bits and Bit Holder, to hold screw driver heads (Slotted and Philips), in hammer drill driver) (2units total) | 1 | 1 | 1 | 3 |  |  |
| 59 | drill bits Masonry (7mm & 8mm) short length about 110cm | 1 | 1 | 1 | 3 |  |  |
| 60 | drill bits Masonry (12mm & 13mm) medium length about 210cm | 1 | 1 | 1 | 3 |  |  |
| 61 | drill bits Masonry (25mm) long length about 410cm | 1 | 1 | 1 | 3 |  |  |
| 62 | drill bit Metal (6-9-10-12-14)mm (5 units Total) | 1 | 1 | 1 | 3 |  |  |
| 63 | Grinding wheels 4.5" and 9" (Metal) | 1 | 1 | 1 | 3 |  |  |
| 64 | Metallic Box or specialized Bag, for hand tools, to contain | 1 | 1 | 1 | 3 |  |  |
| 65 | Industrial cable cutter | 1 | 1 | 1 | 3 |  |  |
| 66 | Insulated combination pliers 160mm | 1 | 1 | 1 | 3 |  |  |
| 67 | straight jaws locking pliers | 1 | 1 | 1 | 3 |  |  |
| 68 | diagonal cutting nippers 160mm | 1 | 1 | 1 | 3 |  |  |
| 69 | Berlin pattern snips | 1 | 1 | 1 | 3 |  |  |
| 70 | claw hammer fiber glass handle | 1 | 1 | 1 | 3 |  |  |
| 71 | engineers hammer glass handle | 1 | 1 | 1 | 3 |  |  |
| 72 | retractable utility knife | 1 | 1 | 1 | 3 |  |  |
| 73 | slotted screw driver set 10 pieces | 1 | 1 | 1 | 3 |  |  |
| 74 | Philips screw driver set 10 pieces | 1 | 1 | 1 | 3 |  |  |
| 75 | Voltage test Driver | 1 | 1 | 1 | 3 |  |  |
| 76 | Measuring Tape 25mm; 10m | 1 | 1 | 1 | 3 |  |  |
| 77 | Measuring Tape 25mm; 5m | 1 | 1 | 1 | 3 |  |  |
| 78 | 20-compartment organizer with removable dividers is optimal for hand tools and small parts. It features a durable polycarbonate lid, carry handle. | 1 | 1 | 1 | 3 |  |  |
| 79 | Cable ends, wire terminals |  |  |  |  |  |  |
| A | 2.5 mm | 100 | 100 | 100 | 300 |  |  |
| B | 6 mm | 300 | 300 | 300 | 900 |  |  |
| C | 10 mm | 200 | 200 | 200 | 600 |  |  |
| D | 25 mm | 100 | 100 | 100 | 300 |  |  |
| 80 | Cable shoes |  |  |  |  |  |  |
| A | 6 mm | 200 | 200 | 200 | 600 |  |  |
| B | 10 mm | 200 | 200 | 200 | 600 |  |  |
| C | 16 mm | 200 | 200 | 200 | 600 |  |  |
| D | 25 mm | 50 | 50 | 50 | 150 |  |  |
| 81 | bag circle cable clips |  |  |  |  |  |  |
| A | 6 mm | 100 | 100 | 100 | 300 |  |  |
| B | 10 mm | 100 | 100 | 100 | 300 |  |  |
| C | 12 mm | 100 | 100 | 100 | 300 |  |  |
| D | 14 mm | 100 | 100 | 100 | 300 |  |  |
| E | 16 mm | 100 | 100 | 100 | 300 |  |  |
| 82 | RJ 45 connectors | 100 | 100 | 100 | 300 |  |  |
| 83 | Metallic Box, to contain | 1 | 1 | 0 | 2 |  |  |
| 84 | self tapping screw flat head 5cm/5mm | 1000 | 1000 | 0 | 2000 |  |  |
| 85 | self tapping screw flat head 1.5cm/300 | 1000 | 1000 | 0 | 2000 |  |  |
| 86 | Palstim Anchors 7mm | 1000 | 1000 | 500 | 2500 |  |  |
| 87 | self drilling screw flat head (small) 13mm | 1000 | 1000 | 0 | 2000 |  |  |
| 88 | self drilling screws with hex head washer 14*1" | 1000 | 1000 | 0 | 2000 |  |  |
| 89 | sleeve anchor bolts with hex bolt 3/8"*1/2"*65mm | 200 | 200 | 0 | 400 |  |  |
| 90 | 8mm (5/16) Heax Head, 6cm, |  |  |  |  |  |  |
| A | Screws | 500 | 500 | 0 | 1000 |  |  |
| B | Nut | 500 | 500 | 0 | 1000 |  |  |
| C | Washer | 1000 | 1000 | 0 | 2000 |  |  |
|  | Other |  |  |  |  |  |  |
| 91 | PVC insulating Tape (10 different colors) | 100 | 100 | 100 | 300 |  |  |
| 92 | Plastic cable ties 30cm packet | 10 | 10 | 5 | 25 |  |  |
| 93 | Delivery to Deir Debuan |  |  |  |  |  |  |
| 94 | Delivery to Nablus |  |  |  |  |  |  |
| 95 | Delivery to Tulkarem |  |  |  |  |  |  |
|  | Total in Euros (TOTAL COST WITH DELIVERY DDP VAT UNPAID) EUR |  |  |  |  |  |  |

LOT 2: 5kWp Grid-tied Solar System - Tulkarem Industrial School

|  |  | Qty |  |  |  |  |  |  |  |  | Unit Price (UNIT COSTS WITH DELIVERY DDP VAT UNPAID) EUR |  |  |  | Total Price (TOTAL COST WITH DELIVERY DDP VAT UNPAID) EUR |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2.1 Photovoltaic Modules | Polycrystalline or Mono-crystalline Modules Minimum rated power 320 W per module Positive Power Output Tolerance Minimum module efficiency @ STC ≥ 15.6% Anti-reflective Glass with Self-Cleaning Layer Aluminum Frame Maximum Ratings; Operational Temperature -40 ~ +85 °C; Maximum System Voltage 1000 VDC; Max Series Fuse rating 15 A IP65 junction box or higher. PV cells should be of grade A Have factory – premounted DC solar connectors MC4 or H4 type. PV panel manufacturer is certified according to ISO 9001 and ISO 14001. At least 10-year product warranty against defects from design, material or workmanship. At least 25-year linear power warranty for min. 82% power output after 25 years, 90% after 10 years IEC 61215, IEC 61730, IEC 61701 & IEC 62716 Certifications Anti-Potential Induced Degradation (PID) according to IEC 62804 Exposed to a Flash Test (Test results will be required) Module manufacturer should be one of the top 10 manufacturers in the Tier 1 ranking Through installation, minimum space between photovoltaic modules from all sides is 0.5 cm. | 16 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.2 Multiple Grid-Connected Inverters | Grid-tied 1-phase inverters 1 unit of 5kWn , (String Inverter) Minimum 2 MPPT Inputs per inverter AC Output Single-phase, Rated Voltage 230V Rated Frequency 50 Hz ± 5 Hz Outdoor Inverters (IP65) with LCD Display Ground Fault Indicator Peak Efficiency > 98%, European Efficiency > 98% Noise Emission < 50 dB @ 1m THD < 3%. The voltage should be calibrated -15%, +10%. Provided with integrated DC load –break disconnect. Compatible with industry –standard monitoring and GSM data communication systems (e.g. Meteocontrol, Fat Spaniel) or similar system provided by the inverter manufacturer. At least 10-year product warranty Certifications; TUV, CE, VDE 0126-1-1, VDE AR-N-4105, AS 4777-2, AS 4777-3, AS 3100, IEC 61727, EN61000-6-1, EN61000-6-3 and EN 50178. The inverter should be communicative via Bluetooth or RS485 The inverters must be protected from direct sunlight and from direct impact of rainfall The inverter should be approved in accordance with the following certificates; VDE AR-N-4105, AS 4777-2, AS 4777-3, AS 3100, IEC 61727 and EN61000-6 - The inverter must be made in Europe - The Inverter Manufacturer must have an Authorized Technical Service center in Palestine or Israel since more than 5 years. |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.3 Monitoring System and Weather Station | Web Based Monitoring system, data logger or imbedded in Inverter. Ethernet port for communication To monitor the inverter and its main parameters. |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.4 Digital kWh Meter-Production Meter | According to Tulkarem Municipality requirements, including 3 phase bidirectional energy meter for the whole school, Indirect with current transformers, and single-phase Energy meter for the production meter. and all required boxes and protections. unless otherwise stated by the Municipality. |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.5 Mounting Structure | Galvanized steel Mounting structure, or Aluminum. To withstand not less than 120km/h wind speed, according to a certified Structural Civil engineer department. No perforating on the roof, the use of prefabricated concrete blocks Not less than 16 units, of weight 70-90kg Tilt angle of the mounting structure must be between 25-30 degrees All Structures must start at an elevation of more than 50cm above the concrete base level. The structure must be treated to remedy any harm or damage to the galvanizing coating |  | L.S |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.6 DC Cable | Solar PV1-F Type 6mm² thickness, two different colors |  | L.S |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.7 AC Cable | XLP Cable 3x10mm² Double insulation, UV resistant, Temperature range: -15 ~ +90 °C Flame retardant according to IEC 60332-1 IEC, TUV, UL, VDE, or KEMA certification |  | L.S |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.8 Cable Protection | All cables from PV strings to inverters, and from inverter to electrical panel and from electric panel to energy meters must be inserted in cable protecting UV resistant conduits Since a probability of severing or damage in cables appears, cables or strengthened conduits will be used Electric cords will respect the code standardized by colors (in direct current the blue thread will be the negative polarity; in alternating current phase: red / brown / black, neutral: blue, PE: green-yellow). To limit the surges due to the lightning, the conductors of positive and negative polarity of the photovoltaic modules have to be contiguous mounted with the equipotential connection. We shall watch that the cables of connection between the photovoltaic field and the electric equipments are stuck on all their length to the cable of mass. A complementary, typical protection sheath or gutter allows to increase the degree of protection. The pathway of electric cables as well as their fixation and that of the other elements as for example the boxes of junction will be realized so as to become integrated, at best, in the concerned buildings, while trying to reduce the lengths. Cables must be correctly fixed, in particular those were exposed to the wind.Cables have to walk in zones beforehand defined or inside mechanical protections. They must be also protected from angular edges. All DC and AC Cables running inside the cable trays and trunks must be inserted into corrugated (with metal) industrial PVC flexible pipes. All DC and AC Cables running indoors must be placed inside appropriate Plastic Trunks. |  | L.S |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.9 DC Panel and Protection | Suitable for outdoor use (IP65) DC Junction Box 24 slots at least. Including DC Breakers and DC Surge arresters (surge protection device) Type II All required cable glands and buss bars included Box with panel. Accessible to the breakers without opening the whole cover. | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.10 AC Panels and Protection | Suitable for outdoor use (IP65) AC line must be double-protected (i.e. inverter-side AC protection and on the side of M.D.B) Appropriately sized 2-pole AC circuit breakers according to international standards, Short circuit current protection General circuit breaker of limit of concession (subscriber's circuit breaker) correctly sized : Appropriately sized Earth Leakage with sensitivity of 30 mA and Overvoltage protection according to IEC requirements Protection equipment must have IEC and TUV certifications AC Surge protection 2 Pole. Includes any required extra breakers at the existing main Electrical Board | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.11 Grounding System | The earthing system should be done according to IEC requirements and according to internationally accepted standards. Interconnection of all the metallic masses of equipments of the installation of production and electricity supply by using green/yellow protection conductors. The earthing system should not be connected to the Grid earthing or Surge protection system The system resistance should be between (2-5) ohms from any location. unless otherwise stated by the municipality. Each PV module shall be grounded (to steel structure) using 10 mm2 cross section cables minimum Steel structure & Inverter shall be grounded (to main earthing box) using at least 16 mm2 isolated copper wires cross section cables All metal components including cable trays must be grounded using 16 mm2 isolated copper wires cross section cables Main earthing cable used to connect the main earthing busbar and the earthing electrodes must be of 16 mm2 isolated copper wires Contractor must ensure continuity of the earthing system One point (bus bar) for the whole system earthing is required. Earthing of the PV system (including all its parts) and earthing for the lightning protection system must be the same as the existing earthing system of the building All Earthing regulations and requirements set by Tulkarem Municipality must be followed. If Electrodes are to be used only Taken Electrodes will be accepted, (copper crest), and every electrode must be inserted into an appropriate Concrete manhole. | L.S |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.12 System Installation & Operation | Complete system installation, commissioning, and testing appropriately and according to the existing local electricity requirements and grid code The inverters should be easily accessible and protected from direct sunlight and from direct impact of rainfall All parts of the solar system (Modules, inverter, protection panels – DC & AC, cables…) must bear warning signs and labels according to local standards and requirements. The installation must follow the requirements of Tulkarem Municipality. Maintenance assistance for a first base instructions is free two years after the implementation. Warranty and Maintenance assistance for a first base instructions is free two year after the implementation | L.S |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.13 Grid Connection | Complete supply, installation and commissioning of a Bidirectional kWh meter panel Suitable for outdoor use (IP65) The Bidirectional meter panel shall be installed at the connection point (Grid-side) Each panel should include the kWh meter, appropriately sized 2-pole or 4-pole AC circuit breaker (main AC MCB), and any other material required to ensure that the panels are installed according to local standards and requirements (the installation must follow the requirements of Tulkarem Municipality | L.S |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.14 Warning Signs | The electric warning signs should be installed on each component of the PV system (inverters, connection and distribution boards, mounting structure, modules …etc.) | L.S |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Total in Euros (TOTAL COST WITH DELIVERY DDP VAT UNPAID) EUR |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

[DDP (Delivered Duty Paid)]  — Incoterms 2010 International Chamber of Commerce http://www.iccwbo.org/products-and-services/trade-facilitation/incoterms-2010/the-incoterms-rules/ .